## Basecase_HS
|  |  |  | Western CO | [5 empty] | New Mexico |  |  |  | Eastern Colorado
Pre Project/ Pre stressing |  |  | notes | WECC | Bus | Unit |  | change | new | WECC | Bus | Unit |  | WECC | Bus | Unit
|  |  |  | Bus No. | Name | ID | 27HS |  |  | Bus No. | Name | ID | 27HS | Bus No. | Name | ID | 27HS
|  |  | While this is retired by 2027 it is left on to preserve its transmission rights | 79015 | Craig 1 | 1 | 375 | 95 | 470 | 10423 | FC_SOL | PV | 152 | 70495 | JMSHAFR1 | G1 | 36.3
TOT2A | 230 MW |  |  | 79016 | Craig 2 | 1 | 375 | 95 | 470 | 10425 | FCSOL_BE | BE | Open | 70495 | JMSHAFR1 | G2 | 35
|  |  |  | 79017 | Craig 3 | 1 | 375 | 95 | 470 | 10633 | Arroy_C1A | 1 | 115.8 | 70490 | JMSHAFR1 | G3 | 33
|  |  | LRS1 | 73129 | MBPP-1 | 1 | 590 |  |  | 10636 | Arroy_BS1 | 1 | Open | 70490 | JMSHAFR1 | ST | 13.2
|  |  | LRS2 | 73130 | MBPP-2 | 1 | 590 |  |  | 10638 | Arroy_C2A | 1 | 115.82 | 70487 | JMSHAFR2 | G4 | 12.8
|  |  |  | 79040 | HAYDEN1 | 1 | 200 |  |  | 10641 | Arroy_BS2 | 1 | 0 | 70487 | JMSHAFR2 | G5 | 14.1
|  |  |  | 79041 | HAYDEN2 | 1 | 280 |  |  | 10491 | LRDSBGG1 | 1 | Open | 70493 | JMSHAFR2 | ST | 5
|  |  |  | 79154 | FLGORG1 | 1 | Open |  |  | 10492 | LRDSBGG2 | 1 | open | 70565 | KNUTSON1 | G1 | 40.4
|  |  |  | 79155 | FLGORG2 | 1 | Open |  |  | 10756 | SLYRCH1_MW1 | 1 | 92 | 70566 | KNUTSON2 | G2 | 40.3
|  |  |  | 79156 | FLGORG3 | 1 | Open |  |  | 10757 | SKYRCH2_MW1 | 1 | 57 | 73532 | LINCOLN1 | 1 | Open
|  |  |  | 79157 | BMESA1-2 | 1 | Open |  |  | 10874 | LAJOY_SE1_WG | 1 | Open | 73533 | LINCOLN2 | 1 | Open
|  |  |  | 79157 | BMESA1-2 | 2 | Open |  |  | 10878 | LAJOY_GE_WG | 1 | Open | 73302 | BRLNGTN1 | 1 | Open
|  |  |  | 79162 | CRYSTAL | 1 | Open |  |  | 10884 | TC1 | 1 | Open | 73303 | BRLNGTN2 | 1 | Open
|  |  |  | 79164 | TOWAOC | 1 | 11 |  |  | 12179 | PEGSPV_GEN | PV | 0 | 72714 | KC_GEN | G1 | 17.2
|  |  |  | 79166 | MOLINA-L | 1 | 3 |  |  |  |  | Total: | 532.62 | 73631 | COHIWND_G1 | W | 42.4
|  |  |  | 79172 | MOLINA-U | 1 | 7 | [6 empty] | 73635 | COHIWND_G2 | W | 7.8
|  |  |  | 72724 | AXIAL_GEN | PV | 0 | [6 empty] | 72703 | CRSL_GEN | W | 100.1
|  |  |  | 72729 | DOLORES_GEN | PV | 0 | [6 empty] | 72719 | CT_GEN | W | 84.9
[6 empty] | total: | 2806 | [6 empty] | 72739 | NIYOL_GEN | W | 186.9
[14 empty] | 70010 | TBII_GEN | W | 27.3
[14 empty] | 70616 | TITAN_S1 | S1 | 42.8
[14 empty] | 70635 | LIMON1_W | W1 | 76.38
[14 empty] | 70636 | LIMON2_W | W2 | 76.38
[14 empty] | 70637 | LIMON3_W | W3 | 76.38
[14 empty] | 70733 | CHEYRGE_W1 | W1 | 20.52
[14 empty] | 70736 | CHEYRGE_W2 | W2 | 41.8
[14 empty] | 70739 | CHEYRGW_W1 | W1 | 51.83
Generation in area | [13 empty] | 70742 | CHEYRGW_W2 | W2 | 50.16
[14 empty] | 70753 | BRONCO_W1 | W1 | 55.71
[14 empty] | 70406 | ST.VR_2 | G2 | 158
Number of Bus | Name of Bus | ID | N/ERIS | output | [9 empty] | 70407 | ST.VR_3 | G3 | 145
[14 empty] | 70408 | ST.VR_4 | G4 | 122
| CRAIG_1 | 1 | NRIS | 470 | Retired but set at full to preserve transmission rights | [8 empty] | 70409 | ST.VRAIN | ST | 316
| CRAIG_2 | 1 | NRIS | 470? | Should these be set at 470? In previous DISIS Craig 1 and 2 were set to 440 and Craig 3 to 460 | [10 empty] | Total: | 1929.66
| CRAIG_3 | 1 | NRIS | 470?
| Axial | PV | NRIS | 145 | Has transmission Service Agreement
| Dolores_GEN | PV | NRIS | 105 | Has transmission Service Agreement
| GRNTMSA_GEN | PV | ?? | ?? (80)
| PEGS |  | NRIS

## Basecase_TOT2AstressedHS
|  |  | Western CO | [5 empty] | New Mexico | [5 empty] | Eastern Colorado
Pre Project/ Post stressing |  | notes | WECC | Bus | Unit |  |  |  | WECC | Bus | Unit |  |  |  | WECC | Bus | Unit
|  |  | Bus No. | Name | ID | Old Gen | New Gen | Change | Bus No. | Name | ID | Old Gen | New Gen | Change | Bus No. | Name | ID | 27HS
|  | While this is retired by 2027 it is left on to preserve its transmission rights | 79015 | Craig 1 | 1 | 375 | 295 | -80 | 10423 | FC_SOL | PV | 152 | 0 | -152 | 70495 | JMSHAFR1 | G1 | 36.3 | 0 | -36.3
Pre TOT2A | 230 MW |  | 79016 | Craig 2 | 1 | 375 | 440 | 65 | 10425 | FCSOL_BE | BE | Open |  |  | 70495 | JMSHAFR1 | G2 | 35 | 0 | -35
Goal | 500 MW |  | 79017 | Craig 3 | 1 | 375 | 440 | 65 | 10633 | Arroy_C1A | 1 | 115.8 |  |  | 70490 | JMSHAFR1 | G3 | 33 | 0 | -33
Needed Gen | 270 MW | LRS1 | 73129 | MBPP-1 | 1 | 590 |  |  | 10636 | Arroy_BS1 | 1 | Open |  |  | 70490 | JMSHAFR1 | ST | 13.2
|  | LRS2 | 73130 | MBPP-2 | 1 | 590 | 550 | 0 | 10638 | Arroy_C2A | 1 | 115.82 |  |  | 70487 | JMSHAFR2 | G4 | 12.8
Actual: | 441.2 MW |  | 79040 | HAYDEN1 | 1 | 200 |  |  | 10641 | Arroy_BS2 | 1 | 0 |  |  | 70487 | JMSHAFR2 | G5 | 14.1
|  |  | 79041 | HAYDEN2 | 1 | 280 |  |  | 10491 | LRDSBGG1 | 1 | Open |  |  | 70493 | JMSHAFR2 | ST | 5
|  |  | 79154 | FLGORG1 | 1 | Open |  |  | 10492 | LRDSBGG2 | 1 | open |  |  | 70565 | KNUTSON1 | G1 | 40.4
|  |  | 79155 | FLGORG2 | 1 | Open |  |  | 10874 | LAJOY_SE1_WG | 1 | Open |  |  | 70566 | KNUTSON2 | G2 | 40.3
|  |  | 79156 | FLGORG3 | 1 | Open |  |  | 10878 | LAJOY_GE_WG | 1 | Open |  |  | 73532 | LINCOLN1 | 1 | Open
|  |  | 79157 | BMESA1-2 | 1 | Open | 0 | 0 | 10884 | TC1 | 1 | Open |  |  | 73533 | LINCOLN2 | 1 | Open
|  |  | 79157 | BMESA1-2 | 2 | Open | 0 | 0 | 12179 | PEGSPV_GEN | PV | 0 |  |  | 73302 | BRLNGTN1 | 1 | Open
|  |  | 79162 | CRYSTAL | 1 | Open | 0 | 0 | 10394 | LEF_G1 | 1 | 147 |  |  | 73303 | BRLNGTN2 | 1 | Open
|  |  | 79164 | TOWAOC | 1 | 11 |  |  | 10395 | LEF_G2 | 1 | 147 |  |  | 72714 | KC_GEN | G1 | 17.2
|  |  | 79166 | MOLINA-L | 1 | 3 |  |  | 10396 | LEF_S1 | 1 | 116 |  |  | 73631 | COHIWND_G1 | W | 42.4
|  |  | 79172 | MOLINA-U | 1 | 7 |  |  | 14914 | FCNGN4CC | L | 383 | 95 | -288 | 73635 | COHIWND_G2 | W | 7.8
|  |  | 72724 | AXIAL_GEN | PV | 0 | 145 | 145 | 14914 | FCNGN4CC | H | 434 | 434 | 0 | 72703 | CRSL_GEN | W | 100.1 | 15 | -100
|  |  | 72729 | DOLORES_GEN | PV | 0 | 105 | 105 | [6 empty] | 72719 | CT_GEN | W | 84.9
|  |  | 79019 | MORRO1-2 | 1 | 0 | 30 | 30 | [6 empty] | 72739 | NIYOL_GEN | W | 186.9
|  |  | 79019 | MORRO1-2 | 2 | 0 | 0 | 0 | [6 empty] | 70010 | TBII_GEN | W | 27.3
|  |  | 72746 | GRNTMSA_GEN | PV | 0 | 80 | 80 |  |  | Total: | 1610.62 |  | -440 | 70616 | TITAN_S1 | S1 | 42.8
|  |  | 1565 | 2022-44 PV | PV | 0 | 199 | 199
|  | Note: Even though this project is NRIS it is dispatched lower to aviod violations. This is a known issue and has to do with the first transisitonal cluster. Ask Curt | 1084 | 2021-06 | PV | 0 | 85 | 85
[5 empty] | total: | 2806 |  | 694 | [6 empty] | 70635 | LIMON1_W | W1 | 76.38
[15 empty] | 70636 | LIMON2_W | W2 | 76.38 | 66 | 0
[15 empty] | 70637 | LIMON3_W | W3 | 76.38 | 71 | 0
[15 empty] | 70733 | CHEYRGE_W1 | W1 | 20.52
[15 empty] | 70736 | CHEYRGE_W2 | W2 | 41.8
[15 empty] | 70739 | CHEYRGW_W1 | W1 | 51.83
[15 empty] | 70742 | CHEYRGW_W2 | W2 | 50.16
[15 empty] | 70753 | BRONCO_W1 | W1 | 55.71
[15 empty] | 70406 | ST.VR_2 | G2 | 158 | 120 | -38
[15 empty] | 70407 | ST.VR_3 | G3 | 145
[15 empty] | 70408 | ST.VR_4 | G4 | 122
[15 empty] | 70409 | ST.VRAIN | ST | 316
[15 empty] | 10756 | SLYRCH1_MW1 | 1 | 92
[15 empty] | 10757 | SKYRCH2_MW1 | 1 | 57
[17 empty] | Total: | 2078.66 | 257 | -242.3

## DISISGen_HS
Using TOT2A stressed case
|  |  |  | Western CO | [6 empty] | New Mexico | [6 empty] | Eastern Colorado
|  |  |  | WECC | Bus | Unit |  |  |  |  | WECC | Bus | Unit |  |  |  |  | WECC | Bus | Unit
|  |  |  | Bus No. | Name | ID | TOT2A_stressed | new | change |  | Bus No. | Name | ID | TOT2A_stressed | new | change |  | Bus No. | Name | ID | TOT2A_stressed | new | change
|  |  |  | 79015 | Craig 1 | 1 | 295 |  |  |  | 10423 | FC_SOL | PV | 0 |  |  |  | 70495 | JMSHAFR1 | G1 | 0
|  |  |  | 79016 | Craig 2 | 1 | 440 |  |  |  | 10425 | FCSOL_BE | BE | Open |  |  |  | 70495 | JMSHAFR1 | G2 | 0
|  |  |  | 79017 | Craig 3 | 1 | 440 |  |  |  | 10633 | Arroy_C1A | 1 | 115.8 |  |  |  | 70490 | JMSHAFR1 | G3 | 0
|  |  |  | 73129 | MBPP-1 | 1 | 550 | 560 | 10 |  | 10636 | Arroy_BS1 | 1 | Open |  |  |  | 70490 | JMSHAFR1 | ST | 13.2
|  |  |  | 73130 | MBPP-2 | 1 | 590 |  |  |  | 10638 | Arroy_C2A | 1 | 115.82 |  |  |  | 70487 | JMSHAFR2 | G4 | 12.8
|  |  |  | 79040 | HAYDEN1 | 1 | 200 |  |  |  | 10641 | Arroy_BS2 | 1 | 0 |  |  |  | 70487 | JMSHAFR2 | G5 | 14.1
|  |  |  | 79041 | HAYDEN2 | 1 | 280 |  |  |  | 10491 | LRDSBGG1 | 1 | Open |  |  |  | 70493 | JMSHAFR2 | ST | 5
|  |  |  | 79154 | FLGORG1 | 1 | Open |  |  |  | 10492 | LRDSBGG2 | 1 | open |  |  |  | 70565 | KNUTSON1 | G1 | 40.4
|  |  |  | 79155 | FLGORG2 | 1 | Open |  |  |  | 10874 | LAJOY_SE1_WG | 1 | Open |  |  |  | 70566 | KNUTSON2 | G2 | 40.3
|  |  |  | 79156 | FLGORG3 | 1 | Open |  |  |  | 10878 | LAJOY_GE_WG | 1 | Open |  |  |  | 73532 | LINCOLN1 | 1 | Open
|  |  |  | 79157 | BMESA1-2 | 1 | 0 | 25 | 25 |  | 10884 | TC1 | 1 | Open |  |  |  | 73533 | LINCOLN2 | 1 | Open
|  |  |  | 79157 | BMESA1-2 | 2 | 0 | 25 | 25 |  | 12179 | PEGSPV_GEN | PV | 0 |  |  |  | 73302 | BRLNGTN1 | 1 | Open
|  |  |  | 79162 | CRYSTAL | 1 | 0 | 20 | 20 |  | 10394 | LEF_G1 | 1 | 147 |  |  |  | 73303 | BRLNGTN2 | 1 | Open
|  |  |  | 79164 | TOWAOC | 1 | 11 |  |  |  | 10395 | LEF_G2 | 1 | 147 |  |  |  | 72714 | KC_GEN | G1 | 17.2
|  |  |  | 79166 | MOLINA-L | 1 | 3 |  |  |  | 10396 | LEF_S1 | 1 | 116 |  |  |  | 73631 | COHIWND_G1 | W | 42.4
|  |  |  | 79172 | MOLINA-U | 1 | 7 |  |  |  | 14914 | FCNGN4CC | L | 95 | 95 | 0 | rebalance TOT2A to 500 | 73635 | COHIWND_G2 | W | 7.8
|  |  |  | 72724 | AXIAL_GEN | PV | 145 |  |  |  | 14914 | FCNGN4CC | H | 434 | 414 | -20 | rebalance TOT2A to 500 | 72703 | CRSL_GEN | W | 15 | 15 | 0
|  |  |  | 72729 | DOLORES_GEN | PV | 105 | [10 empty] | 72719 | CT_GEN | W | 84.9
|  |  |  | 79019 | MORRO1-2 | 1 | 30 | [10 empty] | 72739 | NIYOL_GEN | W | 186.9 | 186.9 | 0
|  |  |  | 79019 | MORRO1-2 | 2 | 35 | [10 empty] | 70010 | TBII_GEN | W | 27.3
|  |  |  | 2027 | 2024-13_PV | PV | 0 | 0 | 0 |  |  |  | Total: | 1170.62 |  | -20 |  | 70616 | TITAN_S1 | S1 | 42.8
|  |  |  | 2024 | 2024-BS_BS | BS | 0 | 0 | 0 | [8 empty] | 70635 | LIMON1_W | W1 | 76.38 | 0 | -76.38
|  |  |  | 2274 | 2024-18_BS | BS | 0 | 0 | 0 | [8 empty] | 70636 | LIMON2_W | W2 | 66 | 0 | -66
|  |  |  | 1964 | 2024-19 | BS | 0 | 0 | 0 | [8 empty] | 70637 | LIMON3_W | W3 | 71 | 0 | -71
|  |  |  | 2075 | 2024-21_PV | PV | 0 | 0 | 0 | [8 empty] | 70733 | CHEYRGE_W1 | W1 | 20.52
|  |  |  | 2044 | 2024-32_BS | BS | 0 | 0 | 0 | [8 empty] | 70736 | CHEYRGE_W2 | W2 | 41.8
|  |  |  | 2445 | 2024-33-BS | BS | 0 | 200 | 200 | [8 empty] | 70739 | CHEYRGW_W1 | W1 | 51.83
[6 empty] | total: | 3131 | 830 | 280 | [8 empty] | 70742 | CHEYRGW_W2 | W2 | 50.16
[18 empty] | 70753 | BRONCO_W1 | W1 | 55.71
[18 empty] | 70406 | ST.VR_2 | G2 | 120
[18 empty] | 70407 | ST.VR_3 | G3 | 145 | 95 | -50
[18 empty] | 70408 | ST.VR_4 | G4 | 122
[18 empty] | 70409 | ST.VRAIN | ST | 316
[18 empty] | 10756 | SLYRCH1_MW1 | 1 | 92
[18 empty] | 10757 | SKYRCH2_MW1 | 1 | 57
[20 empty] | Total: | 1835.5 | 296.9 | -263.38
Con | Branch
| From Number | From Name | To Number | To Name | Circuit | Xfrmr | Violations | Max % Loading Cont. |  | Mitigation
Gore Pass - Hayden 230 | 73057 | OAK CREEK TP | 73072 | GOREPASS | 1 | NO | 1 | 104.16 |  | Uprate Gore Pass - Oak Creek TP - Hayden
Gore Pass - Hayden 230 | 73057 | OAK CREEK TP | 79038 | HAYDEN | 1 | NO | 1 | 107.52
Blue River Gore Pass 230 | 73061 | FRASER | 73296 | FRASER | 1 | YES | 1 | 102.14
Gore Pass - Hayden 230 | 73074 | GREENMTN | 73316 | GREENMT1 | 1 | YES | 1 | 104.54
Gore Pass - Hayden 230 | 73074 | GREENMTN | 73317 | GREENMT2 | 1 | YES | 1 | 105.71
Grand Junction - Montrose 345 | 79042 | HOTCHKIS | 79050 | NORTHFRK | 1 | NO | 1 | 101.13
Meeker - Milk Creek 345 | 79046 | MEEKER | 79056 | RIFLE_UTE | 1 | NO | 1 | 103.72